## Sheet1
Performance Assessment System
PAS Project
Tool to Calculate Non Revenue Water
2016

## Data Input
NRW Calculation tool
Data Input sheet
1. General Information
1.1 Name of Urban Local Body | Bhuj
1.2 Year | 2016
1.3 Population
2. Water supplied from sources
2.1 Own surface source (MLD)
2.2 Ground water source (MLD) | 3
2.3 Bulk treated purchase(MLD)
2.4 Bulk untreated purchase (MLD) | 15
2.5 Length of Raw water pipeline (source to treatment plant) (KM) | 5
Total system input volume (MLD) | 18
3. Water Treatment plants
3.1 Installed Capacity of Treatment Plants (MLD) | 20
3.2 Water quantity treated at treatment plant (MLD) | 14.5
3.3 Length of treated water pipeline (treatment plant to WDS) (KM) | 2
Total treated water (MLD) | 17.5
4. Water distribution
4.1 Water quantity received at distribution stations | 14
4.2 Water quantity distributed from distribution stations | 13
4.3 Water quantity distributed directly in network | 3
4.4 Length of water distribution network (KM) | 200
Total water distributed in distribution network (MLD) | 16
5. Consumer end details
5.1 Number of billed metered connections | 0
5.2 Volume of water billed metered consumption (MLD) | 0
5.3 Number of billed unmetered connections | 12000
5.4 Volume of billed unmetered consumption (MLD) | 10
5.5 Number of free (authorised unbilled) metered connections | 0
5.6 Volume of free (authorised unbilled) metered consumption (MLD) | 0
5.7 Number of free (authorised unbilled) unmetered connections | 500
5.8 Volume of free (authorised unbilled) unmetered consumption (MLD) | 1
5.9 Estimated number of illegal (unauthorised) connections | 700
5.10 Volume of illegal (unauthorised) consumption (MLD) | 0.8
5.11 Consumer metering inaccuracy (MLD) | 0
Total Connections | 13200
6. Financial Information - Operating Expenses
6.1 Regular Staff and administration (Rs in Lakhs) | 12
6.2 Outsourced/Contract Staff Costs (Rs in Lakhs) | 15
6.3 Electricity Charges/Fuel Costs (Rs in Lakhs) | 16
6.4 Chemical Costs (Rs in Lakhs) | 10
6.5 Repairs/Maintenance Costs (Rs in Lakhs)
6.6 Bulk (Raw/Treated) Water Charges (Rs in Lakhs)
6.7 Other Costs (Rs in Lakhs)
Total Operating Expenditure (Rs in Lakhs) | 53
Tariff Details
Fixed tariff - Residential (Rs per connection) | 600
Fixed tariff - Commercial (Rs per connection)
Volumentric tariff - Residential (Rs per KL)
Volumentric tariff - Commercial (Rs per KL)
Financial Information - Operating Revenues
6.8 Arrears at the beginning of previous year (Rs in Lakhs)
6.9 Revenue demand from user charges (Rs in Lakhs)
6.10 Revenue demand from tax/cess - Water Service only (Rs in Lakhs)
6.11 Revenue demand from other revenues (Rs in Lakhs)
6.12 Collection against the current demand (Rs in Lakhs)
6.13 Collection against arrears (Rs in Lakhs)
Total Revenue collected (Rs in Lakhs) | 0
?
?
?
?
?
?
?
?
?

## Water balance
NRW Calculation tool
| Water Balance Diagram |  |  | Bhuj | 2016
|  |  | Billed | Billed Metered consumption
|  |  | Authorised | 0% | Revenue
|  |  | Consumption | 0 | Water
|  |  | 55.56% | Billed Unmetered consumption | 55.56%
|  | Authorised | 10 | 55.56% | 10
|  | Consumption |  | 10
|  | 61.11% | Unbilled | Unbilled metered consumption
|  | 11 | Authorised | 0%
|  |  | Consumption | 0
|  |  | 5.556% | Unbilled unmetered consumption
| System |  | 1 | 5.556%
| Input |  |  | 1 | Non-Revenue
| Volume |  |  | Unauthorised consumption | Water
|  |  | Apparent | 4.444% | 44.44%
| 100% |  | Losses | 0.8 | 8
| 18 |  | 4.444% | Consumer metering inaccuracies
|  | Total | 0.8 | 0%
|  | Losses |  | 0
|  | 38.89% |  | Leakage on transmission mains
|  | 7 |  | 22.22%
|  |  | Real | 4
|  |  | Losses | Leakage and overflows at storage tanks
|  |  | 34.44% | 5.556%
|  |  | 6.2 | 1
Leakage on distribution line and at service connections
6.667%
1.2
Note: All values are in MLD
| 18 MLD |  |  |  | 10 MLD
|  |  |  | 0 MLD |  | 10 MLD
55.56%
10 MLD
| Sources | Treated | Distributed
| 18 MLD | 17.5 MLD | 16 MLD | 1 MLD
0.8 MLD
4 MLD
8 MLD
44.44%
1 MLD
1.2 MLD
Authorised consumption
Apparent losses
Real losses
Unbilled authorised consumption
Billed metered consumption
Billed unmetered consumption
Unauthorised use
Meter
Meter
Revenue water
Non revenue water
System input volume
Revenue water
Lossess from WTP to WDS
Leakage on distribution line and at service connections
Leakage on transmission mains
Lossess from source to WTP
Leakage and overflows at storage tanks
Measures to reduce NRW components

## Performance Indicators
Performance Indicators
A. Water Resources Water Losses Performance Indicators
1 | % Authorized and Unbilled consumption to Total Supply | 5.556%
Authorized and unbilled consumption is expressed as percentage of total water supply. This indicator is used for policy level decisions, for example, government offices also have to pay the water bill is the policy level decision to decrease the percentage of authorized and unbilled consumption.
2 | % Losses from Source to WTP | 2.778%
Amount of water losses from source to WTP is expressed as percentage of total system input. This indicator gives the idea of percentage of water losses from source to WTP. Higher the percentage of this indicator indicates that there are more water losses from source to WTP as compared with other parts of water distribution system. This indicator is used for deciding the strategies for reduction of water losses.
3 | % Losses from WTP to WDS | 8.333%
Amount of water losses from WTP to WDS is expressed as percentage of total system input. This indicator gives the idea of percentage of water losses from WTP to WDS. Higher the percentage of this indicator indicates that there are more water losses from WTP to WDS as compared with other parts of water distribution system. This indicator is used for deciding the strategies for reduction of water losses.
4 | % Losses from WDS to final Consumption | 23.33%
Amount of water losses from WDS to final consumption is expressed as percentage of total system input. This indicator gives the idea of percentage of water losses from WDS to final consumption. Higher the percentage of this indicator indicates that there are more water losses from WDS to final consumption as compared with other parts of water distribution system. This indicator is used for deciding the strategies for reduction of water losses.
B. System Operational Water Losses Performance Indicators
5 | Water losses per Connection (Rs per connections) | 469.697
The basic indicator for expressing the water losses is water losses per connection. It is the real losses expressed in terms of daily volume lost pre service connection. The unit of this indicator is Liter/connection/day. This indicator is useful for target settling and also use for comparisons between systems.
6 | Water losses per length of pipeline (Rs per KM) | 29.9517
Real losses expressed in terms of daily volume lost per length of pipeline. The unit of this indicator is KL/km/day. This indicator is more useful to know the condition of Network. Higher the water losses per km of length indicate the bad condition of network.
C. Financial Water Losses Performance Indicators
7 | Annual cost of Real Losses (Rs) | 18.2556
Real losses expresses in terms of production cost. The cost to produce and supply the next unit of water. The unit of this indicator is rupees. This indicator gives the money loss due real losses.
8 | Annual revenue loss from unbilled authorised and apparent losses (Rs) | 7.2
This indicator gives the amount of rupees lost due to billed authorised and apparent losses. The unit of this indicator is rupees. This indicator gives the amount of revenue loss.

## Guide for data input
Guide for Input Data Calculation
Data elements | Various methods to calculate
2. Water supplied from sources 3. Water supplied from treatment plants 4. Water supplied from WDS | 1. Using flow meter (Fixed or Portable flow meter) Measure the volume using the flow meter 2. Volumetric measurement Volume of water can be calculated based on the water level into the tank 3. Calculate using pump discharge Using the pump discharge, hr of pumping and efficiency of pump; volume of water can be calculated. Pump efficiency should be estimated from actual electricity consumption as against required electricity consumption GO BACK TO DATA INPUT
5.2 Volume of water billed metered consumption | From Zone / ward wise metered and billed water connections to be obtained from ULB’s billing system and volume of metered water have to be extracted from ULB records GO BACK TO DATA INPUT
5.4 Volume of billed unmetered consumption | Billed unmetered consumption can be calculated by doing water quantity measurement in test zone like DMA or representative sample survey. Measurement can be done by installing water meter during measurement period or using the bucket survey method. 1. Calculated using Test zone Whole city is divided into the no. of District metered area (DMA); and from that DMA, one test zone should be very carefully selected which should include all category of housing i.e. HIG, MIG, LIG and slum. From test zone, average water at consumer end should be calculated. 2. Calculated using sample survey In this method, representative samples are selected from the city which covers all category of housing i.e. HIG, MIG, LIG and slum and should cover all ferrule size connection. From that survey average quantity of water per connection according to ferrule size should be calculated. GO BACK TO DATA INPUT
5.6 Volume of free (authorised unbilled) metered consumption | Zone / ward wise metered free water connections and consumption to be obtained from ULB GO BACK TO DATA INPUT
5.8 Volume of free (authorised unbilled) unmetered consumption | Identify the un metered authorised connections from the ULB staff. This component typically includes items such as public stand post, tanker supply, government offices, schools, hospitals, gardens, public toilets, etc. * Water consumption in municipal property (municipal schools, offices, gardens etc.) is calculated as per prescribed norms given in CPHEEO manual for specific use. * For estimation of water supply from public stand post: volumetric flow measurement to be deployed for sample population spread in all water distribution zones with information on supply hours * Water supply through tankers to un covered areas by estimating trips, capacity of tankers and estimating increase in tanker supply in summer seasons GO BACK TO DATA INPUT
5.10 Volume of illegal (unauthorised) consumption | From detail consumer survey of selected test zone or by doing sample survey, estimate % of illegal connection and from that estimate the unauthorized consumption GO BACK TO DATA INPUT
5.11 Consumer metering inaccuracy | Metering inaccuracy can be calculated by doing a sample survey across various meter installations at end users. The composition of the sample shall reflect the various brands and age groups of domestic meters. Based on the results of the accuracy tests, average meter inaccuracy values (as % of metered consumption) will be established for different user groups. GO BACK TO DATA INPUT

## Measures to reduce NRW
Interventions | Components of NRW | List of actions
Short term | Unbilled authorised consumption (Free water supply) | · Policy level decision for reducing free connections or charging them. Installation of meters in free connections
| Unauthorised (Illegal) consumption | · Identification and regularising illegal connections
| Leakage and overflow in storage tank | · Repairs to valves and storage tank
· Install water level indicators
| Losses in transmission line | · Identify and repair transmission leakages
Medium term intervention | Reduce customer meter inaccuracy | · Conduct drive for identification and repairing errors in meters
· Replace meter systematically - beginning with the oldest meters and those in the worst condition
| Leakage on distribution line and at service connections | · Hydraulic modeling
· Create DMAs
· Leak detection survey
· Reengineering of pumping system
Long term intervention | Leakage on distribution line and at service connections | · Installation of meters
· Consumer awareness
· Replacement of service connections with new MDPE pipes
· Replacement of PVC with HDPE
· Replacement of AC pressure pipelines into DI pipes